## Slide 1
CEPC Cryogenic System R&D
Rui Ge / Mei Li
On behalf of CEPC cryogenic system
Jan., 14th, 2022
2022 HongKong IAS HEP workshop
Notes: 1

## Slide 2
OUTLINE
Introduction
Layout of the cryogenic system
Discussion and Comparison on CEPC SRF cryogenic system
Discussion and Comparison on SC magnets cryogenic system
Summary

## Slide 3
主要内容
CEPC Cryogenic System Brief Introduction
  Booster ring:
1.3 GHz 9-cell cavities, 96 cavities
12 cryomodules
3 cryomodules/each station
Temperature: 2K
  Collider ring:
650MHz 2-cell cavities, 240 cavities
40 cryomodules
10 cryomodules/each station
Temperature: 2K
  IR magnets:
4 IR magnets, 32 Sextupole magnets, 36 cryomodules
18 cryomodules/each station
Temperature: 4.5K
Detectors:
2 detector magnets
Thermosiphon cooling
4 Cryo-stations
Refrigeration:4X18 kW@4.5K
Circumference:100km
Layout of CEPC Double Ring
Inj(LSS8)
Cryo-station
Inj(LSS2)
Estr(LSS6)
Cryo-station
Ip_cc(LSS5)
Ip_cc(LSS1)
RF Station(LSS7)
RF Station(LSS3)
Estr(LSS4)

## Slide 4
OUTLINE
Introduction
Layout of the cryogenic system
Discussion and Comparison on CEPC SRF cryogenic system
Discussion and Comparison on SC magnets cryogenic system
Summary

## Slide 5
Warm equipment on the ground:
compressor hall, helium gas tanks
Cold equipment under the ground
Beam tunnel
Gallery tunnel
Refrigerator
cryomodules
2K valve boxes
Shaft
Cryogenic transfer line
Layout of CEPC cryogenic system

## Slide 6
Helium purifier
High pressure helium cylinders
10*100m3 helium gas
Pressure vessels
4*50m3 LN2 Storage Tanks
Recycle screw compressors
Piston compressors
Electrical control system
Helium gas bag
Layout of CEPC cryogenic hall

## Slide 7
1.3GHz cryomodule
650MHz cryomodule
Refrigerator
2K valve box
Beam Tunnel
Gallery Tunnel
Transfer line
Tunnel Cross section

## Slide 8
1.3GHz cavity
cryomodule
650MHz cavity cryomodule
Refrigerator
main valve box
Collider part
Booster part
2K
Valve box
2K
Valve box
Layout of CEPC cryogenic system

## Slide 9
OUTLINE
Introduction
Layout of the cryogenic system
Discussion and Comparison on CEPC SRF cryogenic system
Discussion and Comparison on SC magnets cryogenic system
Summary

## Slide 10
Difference for H50MW and H30MW modes
56 collider modules
Multi-transfer lines length: H30 MW 160m → H50MW 224m

## Slide 11
11000
11000
11000
5000
5000
Compressor group
Cold Box
Main Distribution
Valve Box
Dewar
11000
8000
5000
5000
10
Cryomodules
11000
11000
11000
117000
24000
224000
2K valve boxes
14 cryomodules, 6×650MHZ 2-cell cavities each
Collider Ring
3 cryomodules, 8×1.3GHZ 9-cell cavities each
Booster Ring
Flow chart of SRF CDR Scheme
Sub-tunnel
80000
50MW

## Slide 12
Flow chart of SRF Modif. Scheme
3 cryomodules, 8×1.3GHZ 9-cell cavities each
Booster Ring
14 cryomodules, 6×650MHZ 2-cell cavities each
Collider Ring
11000
11000
11000
5000
5000
Compressor group
Cold Box
Main Distribution
Valve Box
Dewar
11000
8000
5000
5000
10
Cryomodules
11000
11000
11000
117000
24000
2K valve boxes
2K valve boxes
Smaller diameter

## Slide 13: Estimated heat loads for SC cavities-CDR Scheme
Four individual refrigerators (4 × 18kW@4.5K) will be employed for the CEPC cavity cryogenic system.
Higgs Mode 50MW | Unit | Collider |  |  | Booster |  | 
 |  | 40-80K | 5-8K | 2K | 40-80K | 5-8K | 2K
Predicted static heat load per cryomodule | W | 300 | 60 | 12 | 140 | 20 | 3
Cavity dynamic heat load per cryomodule | W | 0 | 0 | 153.59 | 0 | 0 | 13.98
HOM dynamic heat load per cryomodule | W | 20 | 12 | 2 | 2 | 1 | 1
Input coupler dynamic heat load per cryomodule | W | 60 | 40 | 6 | 40 | 3 | 0.4
Module dynamic heat load | W | 80 | 52 | 161.59 | 42 | 4 | 15.38
Each Module total heat load | W | 380 | 112 | 173.59 | 182 | 24 | 18.38
Cryomodule number | - | 56 | 56 | 56 | 12 | 12 | 12
EVB heat loss | W | 50 | 10 | 10 | 50 | 10 | 10
EVB number | - | 40 | 40 | 40 | 12 | 12 | 12
MDVB heat loss | W | 50 | 30 | 30 | 50 | 30 | 5
MDVB number | - | 4 | 4 | 4 | 4 | 4 | 4
Total cryogenic transfer line length | m | 1924 | 1924 | 1924 | 536 | 536 | 536
cryogenic transfer line heat loss per meter | W/m | 2 | 0.5 | 0.3 | 2 | 0.5 | 0.3
Total cryogenic transfer line heat loss | W | 3848 | 962 | 577.2 | 1072 | 268 | 160.8
Total heat load | kW | 27.328 | 7.754 | 10.81824 | 4.056 | 0.796 | 0.52136
Total predicted mass flow | g/s | 82.42 | 152.26 | 373.72 | 13.34 | 12.73 | 18.324
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 | 1.54 | 1.54 | 1.54
4.5K equiv. heat load with multiplier | kW | 3.16 | 10.80 | 53.32 | 0.47 | 1.11 | 2.58
4.5K equiv. heat load with multiplier | kW | 67.29 |  |  | 4.15 |  | 
Total 4.5K equiv. heat load with multiplier | kW | 71.44 |  |  |  |  | 
Total:2460m

## Slide 14: Estimated heat loads for SC cavities-Modif. Scheme
Higgs Mode 50MW | Unit | Collider |  |  | Booster |  | 
 |  | 40-80K | 5-8K | 2K | 40-80K | 5-8K | 2K
Predicted static heat load per cryomodule | W | 300 | 60 | 12 | 140 | 20 | 3
Cavity dynamic heat load per cryomodule | W | 0 | 0 | 153.59 | 0 | 0 | 13.98
HOM dynamic heat load per cryomodule | W | 20 | 12 | 2 | 2 | 1 | 1
Input coupler dynamic heat load per cryomodule | W | 60 | 40 | 6 | 40 | 3 | 0.4
Module dynamic heat load | W | 80 | 52 | 161.59 | 42 | 4 | 15.38
Each Module total heat load | W | 380 | 112 | 173.59 | 182 | 24 | 18.38
Cryomodule number | - | 56 | 56 | 56 | 12 | 12 | 12
EVB heat loss | W | 50 | 10 | 10 | 50 | 10 | 10
EVB number | - | 40 | 40 | 40 | 12 | 12 | 12
MDVB heat loss | W | 50 | 30 | 30 | 50 | 30 | 5
MDVB number | - | 4 | 4 | 4 | 4 | 4 | 4
Total cryogenic transfer line length | m | 728 | 728 | 728 | 136 | 136 | 136
cryogenic transfer line heat loss per meter | W/m | 2 | 0.5 | 0.3 | 2 | 0.5 | 0.3
Total cryogenic transfer line heat loss | W | 1456 | 364 | 218.4 | 272 | 68 | 40.8
Total heat load | kW | 24.936 | 7.156 | 10.45944 | 3.256 | 0.596 | 0.40136
Total predicted mass flow | g/s | 82.42 | 152.26 | 373.72 | 13.34 | 12.73 | 18.324
Overall net cryogenic capacity multiplier |  | 1.54 | 1.54 | 1.54 | 1.54 | 1.54 | 1.54
4.5K equiv. heat load with multiplier | kW | 2.89 | 9.97 | 51.56 | 0.37 | 0.83 | 1.98
4.5K equiv. heat load with multiplier | kW | 64.41 |  |  | 3.19 |  | 
Total 4.5K equiv. heat load with multiplier | kW | 67.60 |  |  |  |  | 
Can reduce 4.04kW heat load compared scheme1
Four individual refrigerators (4 × 18kW@4.5K) will be employed for the CEPC cavity cryogenic system.
4 × 16.85 kW
Total:864m
Total:2460m

## Slide 15
Foreign refrigerator / liquefiers, features: mature and stable industry chain, wide range of users
Linde refrigerator / liquefier series
BEPCII: 2*500W@4.5K（IHEP）
PAPS: 2.5kW@4.5K（IHEP）
HEPS: 2.0kW@4.5K+150L/h（IHEP）
Air Liquide refrigerator/liquefier series
ADS injector I: 1kW@4.5K or 100W@2K
Domestic refrigerator / liquefier
Institute of physics and Chemistry, CAS (FULL CRYO) has: 2kW@20K，10kW@20K, etc.; 2.5KW@4.5K or 500W@2K Has been successfully developed; 10kW@4.5K has planned
Institute of Plasma Physics, CAS: existing 500W@4.5K or 150L / h, 2.2kW@4.5K , planned 5kW@4.5K
Large Helium Refrigerator Market Research
https://mp.weixin.qq.com/s/mNQJin9pgKc9wkowtQA4PA
https://mp.weixin.qq.com/s/Twz8Kk4AUwkvB456RWeuqQ

## Slide 16
中科富海制冷机关于万瓦级大型氦制冷机的研制情况：
Development status of 10kW@4.5K or 18kW@4.5K (CEPC) large helium refrigerator of FULL CRYO company:
先导专项已立项，科技部重大专项都有相关工作部署，预计三年将开发出10kW@4.5K大型制冷机，为cepc做好充分准备;
The pilot project has been approved, and the major projects of the Ministry of science and technology have relevant work deployment, which is expected to be developed in three years 10kW@4.5K Large refrigerator, fully prepared for CEPC.
2.5kW@4.5K已经通过验收，是理化所的工作成果;
2.5kW@4.5K or 500W@2K refrigerator has passed the acceptance this year, and it is the work achievement of the Institute of physics and chemistry.
10kW也是理化所牵头联合富海公司共同研制开发的下一代产品。
10kW@4.5K large helium refrigerator is also the next generation product jointly developed by the Institute of physics and chemistry (TIPC, CAS) and FULL CRYO company.
National refrigerator company status research

## Slide 17
The main specification of large refrigerator
Cold compressor

## Slide 18
Including six 2-cell 650 MHz superconducting cavities, six high power couplers, six mechanical tuners and two HOM absorbers
Cryomodule performance |  | Specification
Number of leakage | He →insulation | 0
 | He →beam pipe | 0
 | Insulation →coupler | 0
 | Insulation →beam pipe | 0
 | Coupler →beam pipe | 0
Alignment x/y inside (Cavities) |  | ±0.5mm
Alignment z inside |  | within 2 mm
Coupler antenna design z |  | within 2 mm
Six 2-cell Cavities Cryomodule | 
Overall length(flange to flange, m) | 8.0
Diameter of Vacuum vessel ,m | 1.3
Beamline height from floor, m | 1.5
Cryo-system working temperature, K | 2
Number of 200-POST | 6
Cryomodule for 650MHz 2-cell cavities

## Slide 19
SRF building
Cryogenic building
Magnet building
Beam test building
X-ray building

## Slide 22
PAPS cryogenic hall

## Slide 23
PAPS RF hall

## Slide 24
Cryomodule for 650MHz 2-cell cavities
A test cryomodule with two 2-cell 650 MHz superconducting cavities has been operated in the PAPS system this year.

## Slide 25
BTCM cooldown
BTCM: 100.7W@2K
Level
Pressure
Temperature
Mass flow
BTCM 2K stable operation
Pressure 31mbar±10Pa
Temperature 2K±0.02K
Total dynamic heat load 300W@2K return gas flow rate
Operation test for 650MHz 2-cell cavities

## Slide 26
Cryomodule for 1.3GHz 9-cell cavities
XFEL / LCLS-II type Cryomodule for High Q Cavity
Design Goals:
Low heat loss
Fast cool down
Cryogenic Group in IHEP has manufactured 58 1.3GHz 9-cell Cryomodules for EXFEL cooperated with local companies.
It’s a good foundation for the optimization design for the CEPC cryomodules.

## Slide 27
Scheme1
Scheme2
0.15W/m single loop transfer line heat loss
RF detailed Process calculation
Collider: after modified, Smaller diameter

## Slide 28
5K~8K TS calculation
Total main supply pipe length is 430 meters, and the heat loss per meter is 0.5 W.
The mass flow of liquid helium needs to be provided by the refrigerator is no less than 51.21 g/s .
Main supply pipe sizes: collider- Di=30.8 mm, Booster-Di=14.6 mm.
Main return gas pipe sizes: collider- Di=85 mm, Booster-Di=23.8 mm.
Branch supply pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.
Branch return gas pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.

## Slide 29
Collider 350m main supply pipe
Heat loss per meter: 2.0 W/m
Total main supply pipe length is 430 meters, and the heat loss per meter is 2.0 W.
The mass flow of liquid helium needs to be provided by the refrigerator is no less than 26.88 g/s .
Main supply pipe sizes: collider- Di=30.8 mm, Booster-Di=14.6 mm.
Main return gas pipe sizes: collider- Di=38.8 mm, Booster-Di=18.8 mm.
Branch supply pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.
Branch return gas pipe sizes: collider- Di=18.8 mm, Booster-Di=14.6 mm.
40K~80K TS calculation

## Slide 30
The time for Cooldown is 120000 second.
Cool-down stage I: The cool-down process of the SRF cavity is from 300K to 100K, and the total cooldown time is 120000 second (33h).
Unsteady-state simulation for the RF cavity cooldown
From refrigerator
to refrigerator
SRF cavity

## Slide 31
a) 260K b) 220K c) 180K
d) 140K e) 100K f) 60K
g) 40K h) 20K
The cooling rate of the superconducting cavity needs to be strictly controlled, and a three-dimensional flow field non-stationary numerical simulation of the cooling process of the 650 2-cell superconducting cavity is performed.
A certain simulation basis is laid for the subsequent automatic cooling.
Global velocity distribution
Non-stationary analysis of superconducting cavity cooling process
Unsteady-state simulation for the RF cavity cooldown

## Slide 32
接下来，超导腔侧还需要确定以下事情：
Next, the following things still need to be determined on the superconducting chamber side.
进行低温系统更为详细的流程计算和优化，以回气△P=0.4kPa压降为条件进行管径优化；
More detailed process calculations and optimization of the cryogenic system, optimization of the tube diameter in terms of return gas ΔP = 0.4 kPa pressure drop.
恒温器结构设计优化（接口尺寸、走向等），恒温器之间常温磁铁的结构确认，与高频组、磁铁组一起协商对接方案
Cryostat structure design optimization (interface size, orientation, etc.), the structure of the room temperature magnet between the cryostat needs to be confirmed with RF group, magnet group .
高性能的多通道低温传输管线的设计与测试研究
Design and testing study of high performance multi-channel cryogenic transfer lines.
多通道低温管线真空隔断的优化设计
Optimization of the design of vacuum isolation for multi-channel cryogenic pipeline
……
Summary of CEPC RF cryogenic system design

## Slide 33
OUTLINE
Introduction
Layout of the cryogenic system
Discussion and Comparison on CEPC SRF cryogenic system
Discussion and Comparison on SC magnets cryogenic system
Summary

## Slide 34
SC magnets cryogenic system overview
IDEA detector
LTS Solenoid
HTS Solenoid
Zhu Zian，Wang Meifen
From Zhu Ying-shun
LTS Solenoid ：
Solenoid located outside calorimeter
Inner diameter 7.2 m, length 7.4 m
Central field：3 T
Superconductor：NbTi
Operation temperature：4.2 K
HTS Solenoid ：
Solenoid located inside calorimeter/less material
Inner diameter 4 m, length 6 m
Central field：2 T
Superconductor：YBCO
Operation temperature：20 K

## Slide 35: Estimated heat loads for SC IR magnets
Two individual refrigerators (2 x 4kW@4.5K) will be employed for the CEPC SC magnets cryogenic system.
 |  | 4.5K main loop |  |  | Thermal Shielding 40~80K | 
Name | Unit | No. | Heat load for each | Heat load | Heat load for each | Heat load
IR SC sextupole magnet | W | 32 | 10 | 320 | 68 | 2176
Valve Box of IR SC sextupole magnet | W | 32 | 20 | 640 | 20 | 640
Current lead of IR SC sextupole magnet | g/s | 32 | 0.1 | 3.2 | 0.1 | 3.2
IR SC magnet | W | 4 | 30 | 120 | 180 | 720
Valve Box of IR SC magnet | W | 4 | 30 | 120 | 30 | 120
Current lead of IR SC magnet | g/s | 4 | 0.5 | 2 | 0.5 | 2
Main distribution valve box | W | 4 | 50 | 100 | 50 | 200
Cryogenic transfer-line | W | 4000 | 0.3 | 1200 | 2 | 8000
Total equiv. heat load @4.5K | W | 14356 |  |  |  | 
Total equiv. heat load @4.5K | W | 14356W+10.4g/s |  |  |  | 
Total equiv. heat load @4.5K | W | 14478 |  |  |  | 
Total equiv. heat load @4.5K with multiplier 1.5 | W | 21717 |  |  |  | 
Cooling capacity of refrigerator@4.5K | W | 2 | 12kW@4.5K | 24kW@4.5K |  | 
Installed power (COP 300W/1W) | MW |  |  |  |  | 
 |  | 4.5K main loop |  |  | Thermal Shielding 40~80K |  | 
Name | Unit | No. | Heat load for each | Heat load | No. | Heat load for each | Heat load
IR SC sextupole magnet | W | 32 | 10 | 320 |  |  | 
Valve Box of IR SC sextupole magnet | W | 32 | 20 | 640 |  |  | 
Current lead heat load of IR SC sextupole magnet | W | 32 | —— | —— |  |  | 
IR SC magnet | W | 4 | 30 | 120 |  |  | 
Valve Box of IR SC magnet | W | 4 | 30 | 120 |  |  | 
Current lead of IR SC magnet | g/s | 4 | 0.5 | 2 |  |  | 
Main distribution valve box | W | 4 | 50 | 100 |  |  | 
Cryogenic transfer-line | W | 4000 | 0.3 | 1200 | 3424 | 1.5 | 5136
Total heat load @4.5K | W |  |  | 2500 |  |  | 5136
Total heat load @4.5K | W |  |  | 2500W+2g/s |  |  | 5136
Total heat load @4.5K | W |  |  | 2523.45 |  |  | 5136
Coefficient |  |  |  | 1 |  |  | 0.05
Total heat load @4.5K | W |  |  | 2523.45 |  |  | 256.8
Total equiv. heat load @4.5K | W | 2780.25 |  |  |  |  | 
Total equiv. heat load @4.5K with multiplier 1.5 | W | 4170 |  |  |  |  | 
Cooling capacity of refrigerator@4.5K | W | 2 | 4kW@4.5K | 8kW@4.5K |  |  | 

## Slide 36
Refrigerator selection | 
Liquefaction | 430L/h
Refrigeration | 2×1.5kW@4.5K
Liquefaction/Refrigeration | 1kW@4.5K & 150L/h
Zhu Zian，Wang Meifen
Heat loads and layout for detector magnet
layout for detector magnet

## Slide 37
2 IPs in CEPC Interaction Region, there are 4 QD0 magnets, 4 QF1 magnets, 4 anti-solenoids and 32 sexupole magnets.
Refrigeration:
2.5kW@4.5K
Plant A. Large refrigerator
Plant B. GM refrigerator
The GM refrigerator’s vibration is unacceptable, besides the electricity power consumption is very high.
The maintenance of the GM refrigerator is very difficult, and failure rate is many times that of a single large refrigerator.
Compressor takes up space and produces vibration and noise in tunnel.
SC magnets cryogenic system

## Slide 38
Power consumption comparison
SC magnet:
10W heat load of each SC magnet
1.5W@4.2K GM refrigerator, needs 8 sets of GM refrigerators/each SC magnet, total 16*8=128 sets
power consumption 7.2kW/each GM refrigerator
16 SC magnets power consumption: 16*8*7.2=921kW
If adopts a large refrigerator, power consumption ~800kW
Therefore, the small GM refrigerator scheme has no advantage in the power consumption aspect.
Considering the operation stability and power consumption of the system, the large refrigerator scheme is selected.

## Slide 39
Flow scheme of Traditional SC magnets
cryogenic system
Compressor group
Cold Box
Main Distribution
Valve Box
Dewar
QD0,QF1, and anti-solenoid
QD0,QF1, and anti-solenoid
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
SM
Valve Box
Detector
to another Detector
1.5kW@4.5K

## Slide 40
Flow scheme of Modified SC magnets
cryogenic system
IR sextupoles have been changed from SC magnets to normal conducting ones and cryogenic system for sextupoles can be eliminated.
The requirement for IR sextupole magnets is updated.
The magnet bore and pole field is reduced.
Conventional sextupole magnet technology can be used (FeCoV pole). Max strength 3886T/m2 is achieved with bore aperture 42 mm. Max current < 200A.
J. Gao
Y.W. Wang

## Slide 41
Flow Chart for CEPC MDI Cryostat (one site)

## Slide 42
The total weight of cryostat is about 2.5 T
IP
反抵螺线管
QD0
QF1
冷屏
Beam pipe
Mechanical Design of CEPC MDI Cryostat

## Slide 43
Support numbers |  |  |  |  | 
convective heat transfer coefficient | 1 | 2 | 3 | 4 | 5
5W m^-2 K^-1 | 268.97 K | 268.98 K | 270.52 K | 282.76 K | 283.32 K
8W m^-2 K^-1 | 273.14 K | 273.14 K | 274.09 K | 285.34 K | 286.65 K
Vacuum chamber---temperature field
1
2
3
4
5
Calculation conditions: the outermost layer is set as convective boundary condition, the surface that the support structure contacts with the helium pool is set as 5K, and the surface that contacts with the cold screen is set as 60K

## Slide 44
Vacuum chamber---stress analysis
最大变形0.1mm@外压1Bar
最大应力69.343MPa@外压1Bar
最大变形0.15mm@内压1.2Bar
最大应力125.73MPa@内压1.2Bar

## Slide 45
接下来，超导磁体侧还需要确定以下事情：
Next, the following things still need to be determined on the superconducting magnet side.
需跟进磁铁机械设计，方案确定后可进行更为详细的低温系统设计
Need to follow up on the progress of multiple technology routes for the magnets, and more detailed design of the cryogenic system can be done after the program is determined.
超导磁铁低温恒温器进行更为详细的结构设计，以及针对低温恒温器进行多维度的流动传热仿真计算，分析流场进而指导优化结构设计，形成闭环设计思路。
More detailed structural design of the superconducting magnet cryostat, as well as multi-dimensional flow and heat transfer simulation calculations for the cryostat, analyze the flow field and then guide the optimization of the structural design to form a closed-loop design idea.
.......
Summary of CEPC SC magnets cyogenic system

## Slide 46
Summary
Previous CDR and TDR works have laid a good foundation for the further design.
For the CEPC cryogenic system TDR design, relevant aspects have been considered , including process scheme, layout, and key equipment design.
Several key technologies (JT heat exchanger platform/cryo-circulating pump/multi-channel Transfer line test platform/Virtual system establishment and automatic control strategy research) are introduced.
Further TDR design is going on. Now it‘s just at the stage of scheme comparison, and there is still a long way to complete the whole TDR design. In the later time, the project team members need to work together to greatly push forward the work, and complete the TDR design on time.

## Slide 47
Thanks for Your Attention！