## Slide 1: Concepts for Gating EPICS Alarm
E. Blomley & J. Gethmann

## Slide 2: KIT Accelerators
  KARA (Karlsruhe Research Accelerator)
      Mix of user operation and accelerator research
  FLUTE (Ferninfrarot Linac- und Test-Experiment)
      Experiment driven without fixed beam schedule
  cSTART
      Storage ring for non-equilibrium physics
      FLUTE and laser plasma accelerator as injector
      Installation starts ~ Mid 2026, commissioning ~ 2027
  Software stack
      EPICS 7 (still Channel Access only)
      Ubuntu (24.04) for terminals & servers
      Most servers run inside VM

## Slide 3: Motivation: Gating Alarms?
  Make “alarms” (dis)appear based on certain conditions
      Kicker magnet OFF  Alarm, ON  No alarm
      But only in injection mode. Otherwise:
      Kicker magnet OFF  No alarm, ON  Alarm,
  “Alarms” in EPICS and this talk:
      The alarm severity and alarm threshold fields of records
      “Alarms” in EPICS can also be seen as notifications:
      Help operators to identify & fix potential issues
record(bi, Kicker:Status:On) {
field(ZSV, “MAJOR“)
field(OSV, “NO_ALARM“)
}
record(ai, Magnet:Current) {
field(LOLO, “5“)
field(LLSV, “MAJOR“)
field(LOW, “8“)
field(LSV, “MINOR“)
field(HIGH, “14“)
field(HSV, “NO_ALARM“)
}
  Not talking about actual (hard-wired) alarms & interlocks: machine protection, personal safety systems, required by regulations, …
          Gating Alarms  Dynamic EPICS notifications to support operators

## Slide 4: Examples
record(bi, Kicker:Status:On) {
field(ZSV, “MAJOR“)
field(OSV, “NO_ALARM“)
}
record(bi, Kicker:Status:On) {
field(ZSV, “NO_ALARM“)
field(OSV, “MAJOR“)
}
If in injection mode
In all other operation modes
record(ai, Magnet:Current) {
field(LOLO, “5“)
field(LLSV, “MAJOR“)
field(LOW, “8“)
field(LSV, “MINOR“)
field(HIGH, “14“)
field(HSV, “MAJOR“)
field(HIHI, “20“)
field(HHSV, “MAJOR“)
}
If beam energy is low
If beam energy is high
record(ai, Magnet:Current) {
field(LOLO, “5“)
field(LLSV, “MAJOR“)
field(LOW, “8“)
field(LSV, “MAJOR“)
field(HIGH, “14“)
field(HSV, “NO_ALARM“)
field(HIHI, “20“)
field(HHSV, “MINOR“)
}
If in machine development mode
record(ai, Magnet:Current) {
field(LOLO, “5“)
field(LLSV, “NO_ALARM“)
field(LOW, “8“)
field(LSV, “NO_ALARM“)
field(HIGH, “14“)
field(HSV, “NO_ALARM“)
field(HIHI, “20“)
field(HHSV, “NO_ALARM“)
}
Kicker On
Magnet Strength

## Slide 5: Use Case: Guide the operator
  Support operator to quickly identify potential issues
  Alarm summaries mapped to navigation menu
  Lead to panel where the issue can be fixed
1. and 2. level alarm hierarchy reflects our navigation
Opening the panel should clearly indicate the alarm (or lead to another panel): Would expect to directly see minor alarm on RF panel
Often not necessary to switch to alarm view!

## Slide 6: System Design
          The task: Design a system which provides such a functionality
Define conditions which in which an alarm should change
Configuration
Deploy
Process the configuration
Monitor conditions and “switch” alarm levels
Execute
Global file
File per IOC
Per record
  XML, YML, ….
Condition
Adjustment
Condition
Central application
Part of IOC(s)
Global
Local
New Alarm PVs
Change existing records

## Slide 7: Configuration – On Record Level
record(bi, Kicker:Status:On) {
field(ZSV, “MAJOR“)
field(OSV, “NO_ALARM“)
info(alarmGate1, “NotInjectionMode“)
info(alarmZSV1, “NO_ALARM”)
info(alarmOSV1, “MAJOR”)
}
record(ai, Magnet:Current) {
field(LOLO, “5“)
field(LLSV, “MAJOR“)
field(LOW, “8“)
field(LSV, “MINOR“)
field(HIGH, “14“)
field(HSV, “MAJOR“)
field(HIHI, “20“)
field(HHSV, “MAJOR“)
info(alarmGate1, „HighEnergyStatus“
info(alarmLSV1, “MAJOR“)
info(alarmHSV1, “NO_ALARM“)
info(alarmHHSV1, “MINOR“)
info(alarmGate2, „MachineOperation“)
field(alarmLLSV2, “NO_ALARM“)
info(alarmLSV2, “NO_ALARM“)
info(alarmHSV2, “NO_ALARM“)
info(alarmHHSV2, “NO_ALARM“)
}
record(bi, Kicker:Status:On) {
field(ZSV, “MAJOR“)
field(OSV, “NO_ALARM“)
}
record(bi, Kicker:Status:On) {
field(ZSV, “NO_ALARM“)
field(OSV, “MAJOR“)
}
If in injection mode
In all other operation modes

## Slide 8: Adjust alarm fields of existing record – using records
record(bi, Kicker:Status:On) {
field(ZSV, “MAJOR“)
field(OSV, “NO_ALARM“)
info(alarmGate1, “NotInjectionMode“)
info(alarmZSV1, “NO_ALARM”)
info(alarmOSV1, “MAJOR”)
}
record(calc, Kicker:Status:On:AlarmCond1) {
field(INPA, “<alarmGate1>“)
field(CALC, “A==1“)
}
record(longout, Kicker:Status:On:AlarmZSV1) {
field(OMSL, “closed_loop”)
field(DOL, “{const: 0} “)
field(OUT, “Kicker:Status:On.ZSV“)
}
record(longout, Kicker:Status:On:AlarmOSV1) {
field(OMSL, “closed_loop”)
field(DOL, “{const: 2} “)
field(OUT, “Kicker:Status:On.OSV“)
}
Instead of records: also external application could do that!
Or an EPICS module?

## Slide 9: Possible side-effects of in-place adjustments?
          In-place adjustments
  EPICS record processing: Look at how alarm propagation behaves
  Phoebus widgets: Do (all) widgets pick up changes and adjust alarm borders etc?
  Does the archiver pick this up and logs correctly?
  How will this look like in the alarm server & logger?
  How about disconnects and restarts?
          Additional alarm records
  EPICS level: value and alarm state now in separate records
  Phoebus: Add all PVs to panels? Use JavaScript??
  Archiver: Again, add alarm PVs also to archive?
  Alarm server & logger?
  How about disconnects and restarts?

## Slide 10: Putting it Together – Our current system
EPICS PVs
JAVA Alarming
CSS Alarming
Layer 2
Layer 3
XML configuration + templating
CSS Alarm Tree
Central XML configuration
Central custom Java application
creating additional alarm records
Change severity of alarm records

## Slide 11: Alternative Approaches
  YML file for each IOC  Python script to parse this  create additional alarm records during/after IOC init
  In-record configuration  process during IOC init (similar to autosave)  generate internal EPICS records which modify the alarm fields of the actual record
  In-record configuration  ChannelFinder picks up INFO fields  ChannelFinder PostProcessor used for central application
  …

## Slide 12: Technology Stack
  Our custom system is in operation for 10+ years, but we cannot maintain or develop the custom Java code anymore
  Scaling to potentially millions of PVs relevant? (not for us)
  Use technology which best fits to us? (No Java nor C++ developer)
  Make use of complex features such as ChannelFinder?
  Try to do it only with EPICS base and EPICS modules to avoid ANY additional dependency?
  Is there interest in the EPICS community?
      If not, we might just go for implementing what is easiest and makes most sense for us

## Slide 13: Quo Vadis?
  We are using gated alarms for a long while.. and plan to continue…
  Need to replace our current system and addition of new accelerator good opportunity
  But before committing to design, resources & time: Looking for feedback!
Community Interest?
Still other approach?
Maybe you do something similar?
Feedback, opinions, discussions?
edmund.blomley@kit.edu