## Slide 1
Slide
1
Tests on Integration of Industrial and Scientific Control Systems for IFMIF-DONES
www.s2innovation.com
Wojciech Soroka

## Slide 2
Slide
2
S2Innovation is a Polish company specializing in delivery of software and control systems solutions for particle accelerators and other complex scientific infrastructures.
Started in 2017 we are working with:
ALBA, CERN, ESS, ESRF, FAIR, IFMIF DONES, MAX IV, Tango Community, SOLARIS, XFEL,

## Slide 3
Cooperation between S2Innovation and IFMIF-DONES
Eurofusion grant: WP20-ENS: Early Neutron Source
Slide
3

## Slide 4
Integration of SCADA systems in a hybrid environment (EPICS + WinCC OA)
  Objective:
  Develop and test a prototype communication interface (“Bridge”) to integrate EPICS with the industrial SCADA system WinCC OA, ensuring both flexibility (research) and certified safety (industry).
  Results:
    Prototype Bridge (Java), co-developed with Siemens WinCC OA support.
    Achieved low-latency, bidirectional communication (12–28 ms).
    MPS requirements for response times <50 ms for safety-critical applications have been achieved.
    Reliability exceeded 99.5% during stress tests.
    Decision taken to rewrite Bridge in C++ to further improve performance and maintainability.
Slide
4

## Slide 5
Integration of SCADA systems in a hybrid environment (EPICS + WinCC OA)
  Conclusions :
    Integration of EPICS and WinCC OA is technically feasible and stable.
    Hybrid architecture combines the advantages of open-source based control systems (EPICS) with industrial SCADA.
    Moving from Java to C++ will increase efficiency and align with industry practices.
  Benefit for DONES:
  Proof that a hybrid EPICS + WinCC OA architecture can work reliably. Reduced technological risk for future integration of research and industrial systems. Provides a certified and scalable path for building DONES control infrastructure.
Slide
5

## Slide 6
Integration of PLC communication with EPICS IOCs
  Objective:
  Analyse the impact of diferent device support/drivers on communication delays between Siemens PLC’s (S7 1200, CPU 1212C / S7 1500, CPU 1513-1 PN) and EPICS IOCs in the Machine Protection System (MPS) architecture.
    Built a dedicated test stand enabling communication between an EPICS server and multiple PLCs.
    Implemented and tested both direct (IOCs <->PLC) and in-direct (IOCs <->MasterPLC <->PLC) communication types.
    Extended testing with added IOCs simulating physical devices to ensure realistic test conditions.
  Results:
    Direct communication:
      S7nodave (S7-1200 / S7-1500) → ~25 ms average latency (best-case, within MPS requirements).
      s7plc (S7-1200 / S7-1500) → 163–178 ms average latency.
      OPC UA (S7-1200) → 470–596 ms, limited by hardware sampling times.
    In-direct communication (via Master PLC controller): adds ~200–500 ms overhead, reducing performance of all protocols.
Slide
6

## Slide 7
Integration of PLC communication with EPICS IOCs
  Conclusions:
    Direct S7nodave on modern PLCs offers the best chance to meet MPS latency targets.
    OPC UA and s7plc showed stable communication, but latency exceeded required thresholds.
    In-direct paths add significant delays and should be avoided for critical signals.
  Benefit for DONES:
  Clear comparative analysis of communication protocols, including their advantages and limitations, enabling an informed choice of the safest and most reliable solution for the Machine Protection System (MPS).
Slide
7

## Slide 8
EPICS to OPC-UA pilot implementation
  Objective:
    Analyse the functionality and performance of OPC UA technology.
    Build a local test stand with both direct (EPICS↔PLC/IPC) and indirect (EPICS↔PLC↔EPICS) communications.
    Evaluate delays for different data types (single-bit, multi-bit, analog) under varied sampling/publishing settings.
    Compare PLC (S7-1200, CPU 1212C) vs IPC (427E with S7-1500, Software Controller CPU 1507S) to assess hardware influence.
  Results:
    Direct communication:
      PLC S7-1200 → ~250 ms average latency (all data types, stable but too high).
      SIMATIC IPC 427E (S7-1500)→ ~15 ms average latency (dramatic improvement, meets MPS target).
    Indirect communication:
      Adds ~200–300 ms overhead (total ~500 ms).
    Parameter tuning:
      Publishing interval dominates performance (200 → 400 ms doubles delay).
      Sampling interval has minor effect. Interface modifications (LLDP/Boundaries): negligible or negative impact on stability.
Slide
8

## Slide 9
EPICS to OPC-UA pilot implementation
  Conclusions:
    Simatic IPC (S7-1500) with direct OPC UA is the best viable option for meeting MPS latency requirements.
    PLC S7-1200 hardware constraints (min. 100/200 ms) make it unsuitable for critical paths.
    Data type has negligible effect – performance depends mainly on hardware and publishing config.
    Indirect communication should be avoided for safety-critical signals.
  Benefit for DONES:
    Provides clear, measurement-based recommendations for using OPC UA.
    Identifies IPC as a superior hardware platform, ensuring low latency and high stability.
    Reduces technological risk by showing which setups to avoid and which deliver reliable performance.
Slide
9

## Slide 10
More details
  We are proud to contribute to the development of knowledge and best practices in the field of control systems. S2Innovation team co-authored a published scientific paper on integrating EPICS and SCADA systems in the context of projects such as DONES.
Slide
10

## Slide 11
Thank You
For Your Attention
Slide
11
Wojciech Soroka
Email: wojciech.soroka@s2innovation.com
Mobile: +48 795 794 676
www.s2innovation.com