## Slide 1: Cryogenics based chilling, energy supply and services for deeper or hotter mines.
Daniel L. Cluff
CEO CanMIND Associates
Fellow Camborne School of Mines
www.deepmining.ca

## Slide 2: Interrelations
Glencore
Funding
Engineering Critique
Real Mine Design
CanMIND Associates
Principle Investigator
Physics Engineering
Concept Development
Highview Power
Liquid Air Energy Storage
Pilot plant
5 MW plant
CEMI
Project Management
Business Acumen
Dearman Engine Co.
Engine Development
Techno-economic Analysis
In Kind Contribution
UDMN
Funding
Industry Network
Commercialisation

## Slide 3: Project Elements
Compressed Air System Design
5 to 10 MWe
Cryogenic Chilling
CFD Modelling
Large UG Equipment
Powered by Dearman Engines
UG Cryogenic
Piping and Storage
Receiver size
Piping
Modularity design
PRU Design
Rapid Response Chilling on Demand
Heat Exchanger

## Slide 4: Why LAES
LAES technology provides plant size economy of scale
Energy storage is an emerging technological niche
The cryogenic liquids are produced on the surface in a standard cryogenic liquefaction plant.
Cryogenic liquid is piped to the depth required
  Depends on mine design decision
  Sent to a central location and chill air in downcast shaft
  Sent to individual levels to chill on demand

## Slide 5: LAES Simplified Schematic
PRU can be placed Underground
5 to 10 MWe
+
Chilling
On Surface
LA to Underground
Storage
Chilling on demand
Heat air
in winter

## Slide 6: 350 kW 2.5 MWH Pilot Plant
Highview Power Slough UK

## Slide 7: Six 3600 tpd O2 plants in China

## Slide 8: LAES Process
A Liquid Air Energy Storage (LAES) system is comprised of a charging system, an energy storage section and a discharging system.
Standard industrial air liquefaction plant
  the electrical grid or a renewable energy project supply the electrical energy.
Air drawn from the ambient environment.
  The process creates liquid air a cryogenic liquid at temperatures near -196oC (78 K).
The liquid air is stored in a low pressure insulated tank.
  Easily accessed energy storage repository
  Low risk to the environment
When power is required
  liquid air is pumped to a high pressure and evaporated through a turbine system.
Capable of providing the pressure necessary
  to power a piston engine or turbine resulting in useful work
  to generate electricity or drive a cryogenically powered vehicle.

## Slide 9: Ancillary Economics Includes Argon, Oxygen Markets Both Continue to Grow

## Slide 10: 700+ l Gaseous Air Per 1 l Liquid Air
Change of State

## Slide 11: A Basic Calculation to Illustrate the Heat Absorbed on Change of State
The heat absorbed per kg of liquid air:
Ambient Ta = 29.85oC (273.15 + 29.85 = 303K)
Cryogenic Tc = 78 K
Latent Heat of vaporisation Lv = 205 kJ/kg
Step 1: The mass “m kg” absorbs ΔQL,
Becomes a gas at or near Tc
ΔQL = mLv = (m kg)(205 kJ/kg) = (m kg)205 kJ/kg
Change of state is approximately 180l (gaseous) / 1l (liquid)

## Slide 12: A Basic Calculation to Illustrate the Heat Absorbed on Expansion
Step 2: Very cold air (≈ 80 K) warms up to Ta
Expansion with heat absorbed ΔQa.
ΔTg = Ta – Tc = 303 – 78 = 225 K
change in gas temperature
ΔQa = mCpΔTg = (m kg)(1.005 kJ/kg-K)( 225 K) = 226.13 kJ/kg
Heat absorbed due to change in gas temperature
ΔQT = ΔQL + ΔQa = mLv + mCpΔTg = (m kg)(451.13) kJ/kg
Total heat absorbed due to change of state and expansion

## Slide 13: For 1 MWr Chilling
  So let ΔQT = 1 MJ
  The total heat absorbed by the ambient air
  The mass of liquid air required is 2.217 kg
  So a liquid flow 2.217 kg/s will provide 1 MWr chilling.
  The density of liquid air is about 870 kg/m3
  So a flow of about 2.55 l (liquid) provides 1MWr
  Final gaseous volume 1899.42 l (gaseous) or 1.9 m3

## Slide 16: Psychrometrics to Liquid Air

## Slide 17: Chilling on Demand Yearly Atmospheric Conditions Sudbury Ontario

## Slide 19: Demand for Liquid Air (tpd) to Create a 12/12 DB/WB oC Environment at 1915 Depth
Gap between daily MAX and MIN
Allows for offsetting of LA production during cheaper electricity rates

## Slide 21: A 2400 tpd plant production frontier when the surplus produced over the least expensive energy cost is redistributed to the peak time cost
Chart: Production Frontier for a 2400 tpd Plant with Time Shifting
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
PRODUCTION | 100 | 100 | 100 | 100 | 100 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100
DEMAND | 37.7683 | 34.9359 | 33.3744 | 31.276 | 29.7795 | 31.6517 | 34.0444 | 40.0118 | 42.5371 | 44.8008 | 48.1317 | 50.1167 | 50.7033 | 52.4721 | 54.4167 | 56.4154 | 56.3146 | 56.5929 | 55.8467 | 55.7442 | 53.8354 | 47.4354 | 47.6071 | 48.3042
SURPLUS | 62.2317 | 65.0641 | 66.6256 | 68.724 | 70.2205 | 68.3483 | 44.2558 | 46.1646 | 52.5646 | 52.3929 | 51.6958

## Slide 22: Summary of the cryogen production and power production

## Slide 23
Summary of the cryogen production and power production implications for a 10 MW PRU
Plant Size tonnes | 1600 | 1800 | 2000 | 2200 | 2400 | 2500
Energy Cost | $3,170 | $2,345 | $1,520 | $775 | $787 | $781
Fan Savings | -$1,271 | -$1,271 | -$1,271 | -$1,271 | -$1,271 | -$1,271
Final Cost | $1,899 | $1,074 | $248 | -$496 | -$484 | -$490
YEAR at this rate | $693,071 | $391,886 | $90,701 | -$180,987 | -$176,752 | -$178,869
MWH paid | 218.84 | 218.84 | 218.84 | 218.91 | 219.04 | 218.98
10 MWH PRU recovered | -120.00 | -120.00 | -120.00 | -120.00 | -120.00 | -120.00
FAN MWH recovered | -10.20 | -10.20 | -10.20 | -10.20 | -10.20 | -10.20
TOTAL | 88.64 | 88.64 | 88.64 | 88.71 | 88.84 | 88.77
Tonnes produced | 1094.00 | 1094.00 | 1094.00 | 1094.33 | 1095.00 | 1094.67
Tonnes required | 1094.12 | 1094.12 | 1094.12 | 1094.12 | 1094.12 | 1094.12
Power Generation | 10 | 10 | 10 | 10 | 10 | 10
Operating Period | 12 | 12 | 12 | 12 | 12 | 12
MWH Produced | 120 | 120 | 120 | 120 | 120 | 120
Efficiency | 54.83% | 54.83% | 54.83% | 54.82% | 54.78% | 54.80%

## Slide 24: Cost of Chilling When Time shifting and Using a Power Recovery Unit

## Slide 25: Plant Configuration Costing
Plant Configuration | Waste heat | Standalone | Standalone | Waste heat
Liquefaction capacity (tonnes/day) | 2500 | 3000 | 2000 | 1700
Power input (MW @ charge time) | 21.4 | 25 | 16.6 | 14.3
Charge time hrs | 6 | 6 | 8 | 8
Consumed energy MWH | 128.4 | 150 | 132.8 | 114.4
Discharge time hrs @ 5 MW | 18 | 18 | 16 | 16
Energy output (MWH) | 90 | 90 | 80 | 80
Liquid air store capacity (tonnes) | 570 | 570 | 510 | 510
Round trip efficiency | 70% | 60% | 60% | 70%
CAPEX (million $) | 46 | 40 | 33 | 38
PRU (turbines/generators/grid) | 8.15 | 8.15 | 8.15 | 8.15
Storage cost | 3 | 3 | 2.7 | 2.7
Cost per kilowatt ($) | 9285 | 8098 | 6569 | 7545
Cost per kilowatt-hour ($) | 516 | 450 | 411 | 472

## Slide 26: Ancillary Systems
Chilling accounts for a major share of consumption
There are a number of other services that can be implemented that provide a service while also simultaneously chilling as a side benefit.
  Compressed air
  Electricity production
  Vehicles, pumps or fans that can be driven by liquid air

## Slide 27: Compressed Air
The production of compressed air exploits the liquid nature of the cryogen, which is simply squirted into a receiver tank and allowed to reach ambient temperature – quickly!

## Slide 28: Compressed Air Supply With Chilling Power
Compressed Air Consumption |  | Receiver Size | Chilling Power | kW ft3/min | Mass flow | Liq flow | Plant impact
ft3/min | m3/hr | m3 | kW |  | kg/s | l/s | tpd
500 | 850 | 1.79 | 124 | 0.248 | 0.29 | 0.33 | 25
1000 | 1699 | 3.6 | 248 | 0.248 | 0.58 | 0.67 | 50
2000 | 3398 | 7.28 | 496 | 0.248 | 1.16 | 1.33 | 100
3000 | 5097 | 11.06 | 744 | 0.248 | 1.74 | 2.00 | 150
5000 | 8495 | 18.54 | 1240 | 0.248 | 2.9 | 3.33 | 250

## Slide 29
Assuming continuous demand the liquid air can be configured to provide a modular compressed air system which will simultaneously chill at the location the receiver tank is located akin to spot chilling.
Chilling Power as a function of the Compressed Air Supply

## Slide 30
In the schematic it was indicated that the PRU could be placed underground.
Part of the PRU process is to pump the liquid air to a pressure of about 1000 psi before evaporating and expanding through the turbomachinery.
At 2000 m the pressure is about 2500 psi
Sufficient pressure to eliminate the pumps
Recall the earlier LAES Simplified Schematic

## Slide 31: Recall the earlier discussion regarding the gap between the MAX and MIN daily temperature was about 500 tpd, Below for a 5 MWe PRU
 | Waste heat | Standalone | Standalone | Waste heat
Liquefaction capacity (tonnes/day) | 2500 | 3000 | 2000 | 1700
Power input (MW @ charge time) | 21.4 | 25 | 16.6 | 14.3
Charge time hrs | 6 | 6 | 8 | 8
Consumed energy MWH | 128.4 | 150 | 132.8 | 114.4
Discharge time hrs @ 5 MW | 18 | 18 | 16 | 16
Energy output (MWH) | 90 | 90 | 80 | 80
Liquid air store capacity (tonnes) | 570 | 570 | 510 | 510
Round trip efficiency (waste heat) | 70% | 60% | 60% | 70%
CAPEX (million $) | 46 | 40 | 33 | 38
PRU (turbines/generators/grid) | 8.15 | 8.15 | 8.15 | 8.15
Storage cost | 3 | 3 | 2.7 | 2.7
Cost per kilowatt ($) | 9285 | 8098 | 6569 | 7545
Cost per kilowatt-hour ($) | 516 | 450 | 411 | 472
Typically the cold would be recycled to cold storage, but here it is absorbed by the air at depth

## Slide 32: Exploitation of the Joule Thompson Effect
With 2500 psi available as a forcing pressure the Joule Thompson Effect, which is part of the liquefaction process, can be exploited to provide further chilling commonly referred to as free expansion or a throttling process.
T2 = T1 - Uj(P1 - P2), P2 = 14.5 psi, T1 = 25oC
where Uj is the JT coefficient - ambient T1 - contained P1
For a contained pressure of 880 psi, Uj = 0.1815
T2 = 298 - 0.1815(880 – 14.5) = 140.9 K =-132.05oC

## Slide 33: CFD Model for Chilling the Entire Airflow, Similar to a BAC

## Slide 34: CFD Model for Chilling the Entire Airflow, Similar to a BAC

## Slide 35: CFD Model Flow Trajectories

## Slide 36: Close up View of Heat Exchanger 1.67 sec

## Slide 37: Close up View of Heat Exchanger 8.2 sec

## Slide 38: Average Temperature of Air in Shaft
Chart: 500 m deep cyl assemb 3.SLDASM [500 m deep [500 m]]

## Slide 39: Cryogenics based chilling, energy supply and services for deeper or hotter mines.
Thank you to:
Glencore for Financial Support and Engineering Excellence.
UDMN for financial support.
CEMI for business expertise and project management
Dearman Engine Company for Cryogenics expertise and technoeconomic analysis.
Highview Power Storage for LAES expertise and technical support.
Camborne School of Mines for academic support
Dr. Daniel L. Cluff
CanMIND Associates
www.deepmining.ca