## Slide 1: Validation and verification of industrial control systems (FTEC2019-11)
Ignacio David López Miguel (BE-ICS-AP)
10/12/2020
Supervisors: Jean-Charles Tournier and Borja Fernández Adiego

## Slide 2: Recap: Applying model checking to PLC programs
…
If Output1 is FALSE
then Output2 is TRUE
AG (!Output1 → Output2)
Requirements
Formalized requirements
Control Flow Automata
Intermediate Model
PLC program
Model checking algorithms

Property failed
Trace leading to the violation

Property OK
PLCverif
Theta

## Slide 3: Tasks performed
Development
Usage
R&D
Improving PLCverif
Using PLCverif in real CERN projects
Finding new ways and projects where formal methods could be used

## Slide 4: Usage
SPS Personnel Protection System
Problems found
Changed priority of the different modes
Missing/wrong conditions
Wrongly documented specification
Simultaneous active state of exclusive signals
 Report issued and problems discussed
Difficulties during the verification
Non-implemented built-in functions
New bugs
Very complex safety functions
Powering Interlock Controllers (PIC) Machine protection  few tests performed. To be continued
Demo presented to UNICOS and external potential client to start using PLCverif

## Slide 5: Development
Issues with different SCL instructions fixed. New features included  always ongoing
PLCverif is now OpenSource (https://gitlab.com/plcverif-oss)
Integration with the latest release of Theta  ongoing
Upgrade from S7-300/400 to S7-1200/1500  been done upon necessities

## Slide 6: R&D
{
Verify C++ code from other sections
Simplification of the Control Flow Automata
Working group about formal methods
Where to apply formal methods? Any critical function:
In house Integrated Circuits (e.g. FPGA)
Embedded Software
Safety systems
Planning/Schedule
What to do?
Sharing knowledge
Understanding the benefits of formal verification
Identifying collaboration