## Slide 1: 11th FTEC Workshop Cryogenics for the HL-LHC IT String
Óscar Durán Lucas
TE-CRG-ME - A. Perin (supervisor), G. Rolando, A. Lees, A. Wanninger, J. Mouleyre, J. Metselaar
CERN, 09th December 2020
INDICO: 981864

## Slide 2: Outline
Overview of the HL-LHC IT String
Cryogenic system for HL-LHC IT String
Update on technical tasks
Heating Unit
Thermal shield circuit
Flowmeter valve box
Update on management tasks
Upcoming activities

## Slide 3: Overview of the HL-LHC IT String
View of LHC and IP5 with location of IT magnets
Integration of IT String in SM18
The final focusing superconducting inner tripplet (IT) magnets of ATLAS and CMS of LHC will be replaced during LS3.
HL-LHC IT String will be installed in SM18 facility for testing the collective behaviour of magnets and systems, get information to speed up the commissioning in the LHC tunnel and configuration of IP5L.
*Images from CRG-TM presentation,
INDICO 797080

## Slide 4: Cryogenics system for HL-LHC IT String
*Images from TCC presentation,
INDICO 891644
SQXL
Magnet cryostat
SQXL
Cold Box
Cold Compressor Unit
String Valve Box
Cryogenic transfer lines
Layout of equipment in SM18

## Slide 5: Heating unit
Why a heating unit in a cryogenic system?
1. After a quench, pressurized (up to 17 bar) and cold (10 to 30 K) He remains in transfer line D and magnet cryostat
Cold Box works at 3 bar → depressurization before restarting cool-down of magnets
Compressor station works with room temperature He
→ Heating of He needed
2. Warm Up
Valve sizing
Pressure model of the system to calculate the pressure drop requirements of the valve
Selection of a Kv able to regulate all operation modes
Technical specifications for tendering:
15 kW electrical heaters
Heater vessels
*Images from previous procurement
Valves, Heaters and Vessels ordered

## Slide 6: Thermal shield circuit valve sizing
Thermal shield supply is divided in 6 parallel circuits with different pressure impedances. Valves need to equilibrate the pressure in the circuit to regulate the flow in all the circuits
Parameters [min, max]: Inlet temperature, inlet pressure, mass flow at each circuit (cold compressor, flowmeter, return module, inner triplet magnets)
Valve control strategy
(x128 cases)
1CV282, CV950 and 1CV288 fully open
CV988
3CV955/2CV955/1CV955
2CV282
All valves sized
1CV282
CV988
2CV282
3CV955
CV950
2CV955
1CV955
1CV288

## Slide 7: Flowmeter internal support
Belleville washer parametric study
Mechanical study for the internal supporting of the Coriolis flowmeters inside a dedicated vacuum box
Finite Element Model (ANSYS Mechanical APDL)
Vertical tie rods holding the weight and horizontal tie rods with Belleville washers (stiff springs) to reduce the vibrations
Tie rod thermal study
Displacements due to cool down contraction
Stress due to cool down contraction

## Slide 8: Management tasks
Instrumentation purchase request
Collection of characteristics for thermometers, pressure sensors and flowmeters
Follow Up of purchase
Documents pool
Collection of all project documents in the sharepoint webpage
Other projects Process Flow Diagrams
SC Link test bench in SM18
Current Leads test bench in SM18
Continue with other management tasks
Meeting organization and minutes
Follow Up of project documentation

## Slide 9: Upcoming activities
Flowmeter box mechanical detailed design
Thermal shield
Vacuum jacket
External supports
Manufacturing details
Installation procedure
Vacuum Barrier in Warm Quench Buffer. Thermal analysis
Earned Value Management (EVM) for the track of the progress and expenses of project
Management tasks
Follow-up of the project (Dashboard, list of approvers, work breakdown structure, purchase)
Meeting organization and minutes
Update and improve project sharepoint webpage
Others

## Slide 10: Thanks for your attention! Questions?
Ó. Durán Lucas, 11th FTEC Workshop, 09.12.2020

## Slide 11
Ó. Durán Lucas, 11th FTEC Workshop, 09.12.2020