## Slide 2: TE-CRG-CE Controls and Electrical Support for cryogenics
Sergio VILLANUEVA
Supervisor: Marco PEZZETTI
SPS BA6
Cryoplant Refurbishment
for CPC6-UNICOS process control system
11th FTEC Workshop

## Slide 3: Summary
Introduction
Control Architecture
Software refurbishment methodology
  Turbine control
  Compressor protection: Sigma Control
Conclusion
Planning

## Slide 4
Refurbishment of the CFB_BA6_QACR Cryoplant
(HW + SW) to be integrated in UNICOS
Introduction: SPS BA6 Layout
Warm He

## Slide 5
SPS BA6 Control Architecture
non-UNICOS
LINDE PLC
CFP-BA6_QAICC
PLC
Kaeser Compressor
+
Sigma Control
(Compressor
Protection)
CS-CCR-COCA
Data Server
Communication
Linde PLC and the Kaeser compressor are currently black boxes.
Hard to operate, maintain and diagnose
Limited supervision
Linde PLC is not UNICOS CERN like.

## Slide 6
SPS BA6 Control Architecture
CFP-BA6_QAICC
PLC
CS-CCR-COCA
Data Server
Communication
New Safety Chain
+ Compressor I/O
Full control/diagnose of all equipments
After the integration, an UNICOS PLC software will control the cryoplant
CFP-BA6-QACR
PLC
New supervision

## Slide 7
SPS BA6 Control Architecture
Updated SCADAs for Compressor and Cold Box.

## Slide 8
Logic Spec.
SPS BA6 Compressor station
+
Cold Box
Database + Logic definition
Unicos
generation
WinCC OA / SW Ready to download
The following procedure has been followed during the development
- TE-CRG-CE standards
- SM18 35 g/s experience
Methodology to upgrade to UNICOS
-TE-CRG-OP / TE-CRG-ML process expertise
Mirror tests
SW validated after mirror test
    (TE-CRG-ML)
    (TE-CRG-OP)
Logic Spec. Draft
(TE-CRG-OP)
- LINDE documentation
  Alarm list
  Functional Plan
  Siemens Software
  P&ID
  Electrical drawing

## Slide 9
Bearing Valve
PV215
Inlet Valve
CV210
Brake Valve
CV211
Brake Temperature
Turbine Speed
Command
SC
TC
MAX
Increment
Setpoint
Turbine block
Speed Sp
Bearing Control
Inlet Increment
Turbine Signals
Geometry
Helium property
Thrust calculation
Integrating 35g/s Turbines
Turbine Speed
Inlet Pressure
Inlet Temperature
Outlet Pressure
Outlet Temperature
A new PLC Function Block has been created to manage all turbine signals / valves
Thermodynamic calculations implemented with Turbine Operational Parameters (TOP)
SM18 35 g/s turbine control taken as a reference
https://edms.cern.ch/document/2337647/1

## Slide 10
Implementation in BA6 turbine string
- Turbines TU1,TU2 in series. 2 turbine blocks:
- Inlet valve 1CV210 output (%) limited by:
○ calculated increments
○ TT219 cooldown limitation
○ Out high limit parameter
1UC
210
2UC
210
LP He
HP He

## Slide 11
Integrating Compressor protection
Kaeser Compressor requires special and dedicated protection
Currently protected by an external equipment, Sigma Control (SC)
+100 alarms/warnings Hard to diagnose
2 proposed solutions : - Keep SC: fastest solution, limited for operation - Remove SC: full integration, electrical modification required
I/O Signals
to the PLC
by Profibus
Sigma Control display
Compressor protection instrumentation
Compressor motor VFD

## Slide 12
Conclusion
SPS-BA6 cryoplant will be ready for commissioning at the beginning of January 2021.
Turbine control will be implemented relying on the experience in SM18 35g/s turbines.
We can easily switch the software to communicate with Sigma control or read instrumentation from the CP and control to VFD.
After several mirror tests, it has been obtained a PLC software that guarantees the most efficient quality control system.

## Slide 13
Thank you for your attention!