## Slide 2: TE-CRG-CE Controls and Electrical Support for cryogenics
Sergio VILLANUEVA
Supervisor: Marco PEZZETTI
SPS BA6
Cryoplant Refurbishment
for CPC6-UNICOS process control system
12th FTEC Workshop

## Slide 3: Summary
Introduction
SPS BA6 Cryoplant status
Ongoing projects.
Conclusion.

## Slide 4
Refurbishment of the CFB_BA6_QACR Cryoplant
(HW + SW) to be integrated in UNICOS
SPS BA6 Layout
Warm He

## Slide 5
SPS BA6 Control Architecture
CFP-BA6_QAICC
PLC
CS-CCR-COCA
Data Server
Communication
New Safety Chain
+ Compressor I/O
Full control/diagnose of all equipments
After the integration, an UNICOS PLC software will control the cryoplant
CFP-BA6-QACR
PLC
New supervision

## Slide 6
Logic Spec.
SPS BA6 Compressor station
+
Cold Box
Database + Logic definition
Unicos
generation
WinCC OA / SW Ready to download
The following procedure has been followed during the development
- TE-CRG-CE standards
- SM18 35 g/s experience
SBS BA6 Software Continuous Integration
-TE-CRG-OP / TE-CRG-ML process expertise
Mirror tests
SW validated after
mirror test
Logic Spec. Draft
(TE-CRG-OP)
- LINDE documentation
  Alarm list
  Functional Plan
  Siemens Software
  P&ID
  Electrical drawing
Validation in progress
(ends June-2021)
Documentation
and software update
Once the validation is finished, the software should be tested on site:
Equipment protection and safeties.
Alarms and interlocks.
Control logic (paying special attention in compressor/turbine system).

## Slide 7
Ongoing Projects. NP02 Test box
NP02 new Test box instrumentation (56 I/O)
NP02 new filter instrumentation (12 I/O)
Level S2
Level 1/2
Level S/R
New NP02 Test box will be located in the pit on 3 levels
Condenser
Purifier
Filter
Test box
The existing NP02 PLC Program will be modified.
- 3 Electrical proposals already presented.
- Cabinets spare I/O channels will be used for this project
- Control preparation will start soon
- Commissioning in August 2021.

## Slide 8
Electrical design and control of the new SC-Link current leads test bench.
Ongoing Projects. SM18 SC-Link
Planning 2021:
May-June Electrical schemas
Aug-Sept Cabinet construction
Oct-Nov Electrical installation +
Control / SW preparation
Dec 2021 Commissioning
Brand new CPU S7-1500 for the control system.

## Slide 9
Ongoing Projects. PN-PA new architecture
Simatic Compact Field Unit (CFU)
Profinet PN
Profibus PA
Simatic CFU
Simatic CFU (with housing) | 2000.00 €
Simatic CFU (without housing) | 1700.00 €
Easy HW and mapping in TIA Portal
PDM Configuration and diagnose
Cheaper for small networks
Integration in 1 single module
Faster speed + ring redundancy
S7-1500 CPU
IE/PB link + 2x FDC157 PA
Profinet PN
Profibus DP
Profibus PA
Distributor AFD8
IE/PB Link PN-PB Gateway | 870.00 €
FDC157 PA Coupler | 2x 800.00 €
AFD8 Distributor PA | 860.00 €
 | 3330.00 €
Better price as the PA devices increases ( >24xPA)
Profibus ring redundancy
Profibus configured in S7 HW Config (not TIA)
PDM Configuration and diagnose
Extra Hardware in the topology (Gateway + coupler)
2 different architectures
(up to 8 PA slaves per module)

## Slide 10
Simatic Compact Field Unit (CFU)
Profinet PN
Profibus PA
Simatic CFU
Simatic CFU (with housing) | 2000.00 €
Simatic CFU (without housing) | 1700.00 €
Easy HW and mapping in TIA Portal
PDM Configuration and diagnose
Cheaper for small networks
Integration in 1 single module
Faster speed + ring redundancy
SC-Link will be the first cryogenic project built with TIA Portal (CPU S7-1500).
S7-1500 CPU
Many field devices (valve positioners and instruments) with be in a Profibus PA Network.
Currently, a new distributor (SIMATIC CFU) is being tested to be integrated in future TIA Portal projects.
Ongoing Projects. PN-PA new architecture

## Slide 11
Conclusion
SPS-BA6 cryoplant software is nearly validated and will be ready to test on site soon with minor electrical modifications (depending on operation schedule)
Neutrino Platform NP02 test box electrical design, software and SCADA preparation has already started (Commissioned in August 2021)
SM18 SC-Link Electrical schemas design is ongoing. Control will be prepared soon (October 2021) This testbench should be commissioned in December 2021.

## Slide 12
Thank you for your attention!