## Slide 1
Ralph Lange, ITER Organization
OPC UA Device Support Overview and Status

## Slide 2: Why OPC UA?
Industrial standard (2006) to interface SCADA to PLCs
  Covers data, alarms, events, historical data, remote methods
Based on OPC Classic (Microsoft; 1996), plus
  Portability
  Safety (authentication, encryption)
  Information modeling (user defined structures)
Gaining momentum in industrial context as universal integration standard
Siemens S7-1500 series PLCs include an embedded OPC UA server

## Slide 3: EPICS Device Support
Based on commercial C++ Client SDK
  Vendor: Unified Automation (~3.5k€ for sources and 1yr support)
  Binaries can be distributed royalty-free
  Platforms: Windows and Linux
Prototype by Bernhard Kuner (HZB / BESSY II)
ITER use cases tested by F4E (Spain) and TCS (India):
  Against S7-1516/1518 embedded OPC UA server
  Against WinCC-OA embedded OPC UA server

## Slide 4: Status
Requirements Specification v1.0 reviewed and agreed: https://bit.ly/opcua-srs-10
Design done (no formal doc yet)
Implementation in progress, “usable pre-release” state
  All basic data types and arrays thereof (read/write/subscribe)
  User-defined structures (read/subscribe)
  All applicable record types in EPICS Base
Used in production at ITER, BESSY II

## Slide 5: Roadmap
Soon:
  Support for server-side queues (sample faster than publish)
  Writing of user-defined structures
Later:
  Read time stamps from within data structure
  Support for OPC UA methods (remote execution of PLC FBs)
  Support for (free) open62541 client library
Under EPICS license, upstream repository on GitHub: https://github.com/ralphlange/opcua