## Slide 1: Study on EPICS Communication over Long Distance
L. Lobes1, R. Lange2, O. Semenov3, D. Stepanov2
1 Tomsk Polytechnic University, Lenin av. 30, 634050 Tomsk, Russia
2 ITER Organization, Route de Vinon-sur-Verdon, CS 90 046, 13067 St. Paul Lez Durance Cedex, France
3 Institution "Project Center ITER", Kurchatov sq. 1, Building 3, 123182 Moscow, Russia

## Slide 2: General test algorithm
Already connected Remote participants:
Troitsk, RUSSIA, IPSec VPN, ping around 69 ms
San Diego, USA, IPSec VPN, ping around 160 ms
Rokkasho, JAPAN, L2 VPN, ping around 250 ms
Mainly tests results presented in this presentation was obtained with Troitsk, RUSSIA and USA San Diego.
Japan in plans in near future.
All remote participants will be watchers only, with no control possibility

## Slide 3: Program execution sequence
set up the generator. The generator generates files for EPICS and also generates a list of the same PVs in a text file(PV_list.txt) for using by Treader program
Compile simple maven project which contain only one IOC.
Start the IOC and start the reading program
Data analysis and processing

## Slide 4: EPICS DB, Control part
Main control record:
Reset timers value record:
record(mbbo, "MSC:TP") {
field(DESC, "Counters period controll record")
field(OUT, "MSC:T-0.SCAN")
field(ZRST, "off") field(ZRVL, "0")
field(FVST, "2 second") field(FVVL, "5")
field(SXST, "1 second") field(SXVL, "6")
field(SVST, ".5 second") field(SVVL, "7")
field(EIST, ".2 second") field(EIVL, "8")
field(NIST, ".1 second") field(NIVL, "9")
record(bo, "MSC:RESET") {
field(DESC, "reset timers")
field(VAL, "0")
field(ZNAM, "GO")
field(ONAM, "RESET")
}
EPICS DB consist of configurable number of counters(Timers).

## Slide 5: EPICS DB: Timers part
record(calc, "MSC:T-0"){
field(CALC, "B?0:val+1")
field(SCAN, "5 second")
field(FLNK, "MSC:T-1")
field(INPB, "MSC:RESET")
}
record(calc, "MSC:T-1"){
field(CALC, "B?0:val+1")
field(SCAN, "Passive")
field(FLNK, "MSC:T-2")
field(INPB, "MSC:RESET")
}
Up to 4000 records
record(calc, "MSC:T-4000"){
field(CALC, "B?0:val+1")
field(SCAN, "Passive")
field(FLNK, "MSC:T-4001.PROC CA")
field(INPB, "MSC:RESET")
}
record(calc, "MSC:T-4001"){
field(CALC, "B?0:val+1")
field(SCAN, "Passive")
field(FLNK, "MSC:T-4002")
field(INPB, "MSC:RESET")
}
Every 4000 PV:

## Slide 6: Timers reading program(TReader)
TReader is control:
Timers update frequency
Reading time
Number of timers to subscribe
Thread quantity
Only writing to RAM while reading data, no other tasks occur here
The program analyzes data and calculates several metrics

## Slide 7: Test Metrics
TReader measure several metrics during the test:
PV value order metric
Connection time – time between star connection and connection complete.
Latency of update MAX – maximum time between the same event on the EPICS server and on the client
Latency of update AVG – average time between the same event on the EPICS server and on the client
Latency of update MIN – minimum time between the same event on the EPICS server and on the client
Server – Server update time MAX AVG MIN – time between update the same PV on EPICS server side
Client – Client update time MAX AVG MIN – time between update the same PV on client side

## Slide 8: PV value order metric
The IOC timers is incrementing by 1 in each update, if there is a difference in neighborhood points on client side read data it is marked as an error.

## Slide 9: Channel latency compensation algorithm
Channel latency from ITER to RF RPC in used VPN channel is 69 ms.
Latency measured by compare EPICS time stamp is around 34 ms.
record(bi, "MSC:JITTER") {
field(DESC, "time jitter")
field(VAL, "0")
field(ZNAM, "0")
field(ONAM, "1")
}

## Slide 10: Average Server-Client time latency, Results (1 stream)
Time in ms.
[PVs, Freq(Hz)]
Remote channel latency compensated

## Slide 11: Average Server-Client time latency LOCAL
Time delay ms.
Time stamp.

## Slide 12: Average Server-Client time latency REMOTE
Time delay ms.
Time stamp.
Remote channel latency compensated

## Slide 13: [10000 PV 1Hz] Server Client time latency REMOTE
Time delay ms.
Time stamp.

## Slide 14: Loss data cases, Server-client time latency chart
data loss here

## Slide 15: Loss data cases, client-client update time chart
The same place as on the previous slide
Everything on time
Everything on time
Data loss

## Slide 16: Loss data cases, client-client update time chart
A more serious case [7000 PV, 5Hz ]
Everything on time
Everything on time
Data loss
about 10 seconds of not good user experience in the center and few seconds in the beginning.

## Slide 17: Multithreading effect
1 Thread
32 Thread
The rest 2% is upper
The rest 2% is upper
8000 PVs, 1 Hz
Time, ms
Time, ms

## Slide 18: Long term test
Treader-long is control:
Timers update frequency
Reading time
Number of timers to subscribe
Thread quantity
writing to DISK when error event is occur
tracked only PV value order metric

## Slide 19: 24 Hours EPICS test result, 10 000 PVs 10Hz update rate, 16 reading streams. IO-RF
Long-term EPICS reading test

## Slide 20: 24 Hours EPICS test result, 10 000 PVs 10Hz update rate, 16 reading streams. IO-US
Long-term EPICS reading test

## Slide 21
VPN channel load during the testing

## Slide 22
 | Maximum PV without major errors events. | 
Frequency, Hz | IO->RF (less than 5 events per day) | IO->US (less than 5 events per day)
10 | 2 000 | 10 000
5 | 6 000 | 10 000
2 | 10 000 | 10 000
1 | 10 000 | 10 000
Summary results of long term experiments

## Slide 23
Practical use case
The practical application of the EPICS over long distances is the organization of remote terminals. As part of work on remote participation in ITER, a remote terminal was organized in RF RPC, technically absolutely identical to those that are installed at ITER site. Tests have shown that the user experience is quite identical to what we have on the ITER side, of course, with the remark that the remote operator can only observe.

## Slide 24: Summary
Summary result:
During testing, no problems were noticed with the number of PV less than 2000.
Since remote centers cannot control any processes, they can only observe, short-term data loss does not affect much to user experience.
Multithreading gives a good performance boost in terms of latency update time.
Cases of data loss do not depend on the test parameters, and from time to time they occur, which makes it possible to assume that something is happening in the channel.
The latency of updates on the side of the remote participant, adjusted to the static network delay due to distance, was demonstrated to be comparable to the latency of local execution. This suggests that EPICS over long distance is quite usable for the purpose of ITER remotes participation tasks.