## Slide 1: GEOMAGNETICALLY INDUCED CURRENTS IN POWER SYSTEMS
Shield Wires effect on GICs in power network and design of an instrument to monitor GICs
Study funded by FCT under project MAG-GIC: PTDC/CTA -GEO/31744/2017
Rute Rodrigues Santos, M. Alexandra Pais, João Cardoso, Miguel Silva, Joana Alves Ribeiro, Fernando Pinheiro

## Slide 2: Geomagnetically Induced Currents in Power Systems
Credits to Joana Alves Ribeiro

## Slide 3: The importance of GICs mitigation
Numerous records of voltage sag, premature ageing of transformers and in some cases regional outages.
From Marusek, 2007
GIC – Sources Forecasting
GIC Modelling
To predict the flow of high GICs in the transmission network
GIC Measuring
To validate the models
GIC – Hazards Prevention

## Slide 4: 1. GIC Modelling
The effect of the Shield Wires

## Slide 5: Shield Wires
Protect the power transmission line from the effect of lightning
Extra path for GICs

## Slide 6: Model for analysing the effect of shield wire on GIC
power line resistance
induced emf along the power line
induced emf along each shield wire span
resistance of each shield wire span line
grounding resistance at each tower
transformer wiring resistance
substation grounding resistance

## Slide 7: In Portuguese Network
In Portuguese Power Transmission Network, first initial tests on single lines gave errors of 5% for a short line, if shield wires were not considered.
When combining different lines, the effect may increase.
It is important to study this effect and understand if it is necessary to include shield wires in the GIC calculation models

## Slide 8: How can we simplify this study?
Getting a simpler circuit!
In which it would be sufficient to deal with a Thévenin equivalent circuit connected to each substation, as shown on the left

## Slide 9
Results from a simulation in a complex power network.
Only the effect of the resistance of shield wires has been considered.
Credits to Joana Alves Ribeiro

## Slide 10: 2. GIC Measuring
The design of an equipment to monitor GICs

## Slide 11: GIC Acquisition System

## Slide 12: Instrument to monitor GICs
The first prototype will be installed to measure the neutral point current on a transformer, at a substation belonging to the national transmission system operator (REN)
Voltage dependence on current intensity
Sensor calibration curve

## Slide 13
Substation Paraimo

## Slide 14
Thank you. Any questions? You can contact me: rute2rodrigues@gmail.com